PROJECT	(INSERT PROJECT NAME)

APPLICATION	GENERAL OFFICE ENVIRONMENT

ACCESS FLOOR	JINDAO® - FS1250B 'EXTRA HEAVY GRADE' SYSTEM

Specification Details

Panel Type	Jindao FS1250B Cementitious Infill Steel Access Panel &

Understructure	Jindao FS-B-PST Understructure at ........... mm finished floor height.

Description of FS1250B Access Floor System

The FS1250B 'Extra Heavy Grade' Access Floor System forms a rigid membrane by safely locking the panels in position, from above - by corner fixing screws. This locking system creates a stringerless access floor that is capable of withstanding normal static and dynamic loads experienced in the majority of general office environments.

Performance Summary

| Application | A general office environment where people, workstations and normal office equipment will occupy the space. The space is likely to be subject to extra heavy equipment loads, normal levels of foot traffic and extra heavy infrequent rolling loads in the office corridors and aisleways. |
| --- | --- |
| Performance | The access floor will be Extra Heavy-Grade, with a safety factor of three times the concentrated (design) loan, and is capable of meeting extra heavy static and dynamic loads per MOB PF2 PS/SPU Platform (Raised Access) Floors Performance Specification. |
| Finished Floor Height | The finished floor height of the access floor, measured from the sub-floor to the top surface of the installed access floor, shall be as shown in the contract drawings. |
| Surface Finish | The access floor shall have a 'bare' panel surface finish ready to accept on-site floor covering supplied by others. |
| Installation | The access floor will be rigid, free from vibration and rocking panels within a 3.0mm level over the entire space. Panels will be accurately cut to fit around all permanent features. |
| Fire Rating | All panels are to provide zero fire hazard indices under MOB PF2 PS/SPU Platform (Raised Access) Floors Performance Specification – Fire and Safety Requirements. |
| Maintenance | All whole panels will be interchangeable allowing for any future changes. The access floor will maintain these original conditions when runs of panels have been removed for normal underfloor access. |

Performance to Standards Guide per MOB PF2 PS/SPU Platform (Raised Access) Floors Performance Specification

| Panel Type | Panel Grade | Dynamic Load (kN) | Concentrated Load (kN) | Impact Load (kG) | Safety Factor | Uniform Load (kN/m2) | Weight (kG) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| FS1250B | Extra Heavy | 5.5 | 5.5 | 50 | 3 | 30 | 16 |

1. GENERAL

Work Included

The access floor contractor shall provide submittals, materials and installation of the access floor system as shown on the contract drawings and as specified in this document.

Related Work Not Included

The builder or general contractor shall provide clear access, dry secure storage and a clean sub-floor area which is free of construction and other trades debris during the installation of the access floor system.

The area to receive the access floor shall be enclosed and be maintained at a temperature range of 5ºC to 32ºC in a relative humidity range of 20% to 70%.

The concrete sealer (if any) shall be compatible with the access floor pedestal adhesive.

The electrical contractor shall provide necessary material and labour to electrically connect the access floor to the building earth.

System Description

The access floor system shall consist of interchangeable square panels of a nominal 600mm x 600mm dimension. The panels shall be selected to meet specific load requirements as detailed in Part 3 of this specification.

The panels shall be supported by adjustable pedestal assemblies, which will positively locate panels to create a rigid membrane.

The understructure system will be as defined under Part 2 of this specification.

The finished floor height of the system above the sub-floor shall be as shown in the contract drawings.

Shop Drawings and Product Data

The access floor contractor shall submit drawings showing the complete access floor system including floor panel layout and all accessories that are part of the system.

The access floor contractor shall submit details and descriptive notes for finished components, anchoring, edge details and interfaces with adjoining work.

Samples

The access floor contractor shall submit for approval one full-size floor panel with finished surface and understructure components for each type of access floor system being supplied.

Quality Assurance

The access floor contractor shall provide a Quality Assurance Plan, which demonstrates that the installed product meets the requirements of this specification.

2. PRODUCT & SYSTEM REQUIREMENTS

Access Floor Panels

The panels shall be 600mm x 600mm in size and shall be interchangeable with other panels except where cut for special conditions. The panels shall be easily removed and replaced without disturbing adjacent panels, by one person using a portable lifting device.

The panels shall consist of a full hard steel top sheet and a die formed bottom pan with a corrosion resistant protection, inside and out, filled with a structural concrete composite core.

The panels shall be rigid structural assemblies, fabricated to size with a size and squareness tolerance of 0.25mm and a flatness tolerance of 0.5mm measured on a diagonal across the top of the panel.

Each corner of the panel shall be formed to accept a single locking screw designed to secure a single corner of each of four adjacent panels at the pedestal head.

Understructure System

The understructure system shall consist of steel pedestal base and steel head assemblies fabricated with the manufacturers standard corrosive resistant finishes. All components are to be factory assembled. Pedestal bases shall be no less than 10,000 mm² in foot print area.

The assembly shall be fabricated with sufficient height to provide the required underfloor clearances shown on the contract drawings.

For finished floor heights of 150mm and over, vertical adjustment shall be accomplished over a range of not less than 25mm without requiring the rotation of the pedestal head.

For finished floor heights less than 150mm a minimum of 10mm adjustment is required.

The pedestals will be provided with a means of levelling and locking the assembly at a selected height, which requires a deliberate action to change the height setting, and which prevents vibration displacement.

Accessories

Air Grilles are to be provided in locations and sizes as detailed on the contract drawings.

Service Outlets are to be provided in locations as detailed on the contract drawings. The outlets will accommodate power, communications, and data signals.

The access floor contractor shall provide the standard steps, ramps, and fascias in locations and as detailed on the contract drawings.

The access floor contractor shall provide .......... spare floors panels and .......... square metres of understructure system for each type used in the project for maintenance stock. These spares shall be delivered to the project in manufacturers standard packages clearly marked with the contents.

The access floor contractor shall provide .......... number of panel lifting devices.

Other accessories to be provided by the access floor contractor should be listed and defined here.

3. PERFORMANCE REQUIREMENTS

The access floor system shall meet or exceed all of the Specific Performance Requirements set out below:

General

All components shall be protected against corrosion with the manufacturers standard factory applied protective finishes.

MOB PF2 Standard

The entire access floor system under this specification shall meet or exceed all of the requirements for Extra Heavy Grade under MOB PF2 PS/SPU Platform (Raised Access) Floors Performance Specification.

Impact Load

An impact load imposed on the access floor system by dropping a 45kg mass from a 900mm height onto a 25mm x 25mm square indentor shall not create structural failure.

Fire Hazard

The panels, without floor coverings, shall provide zero indices for ignitability, spread of flame, heat evolved and smoke developed. These indices shall not change when the panel is cut.

Occupational Health & Safety

The access floor system shall not include any toxic substances, which could prove harmful to building occupants, nor shall it create dust or contaminants, which are harmful to personnel or equipment.

Panel Weight

The panels shall not exceed 16 kg in weight.

4. QUALITY ASSURANCE & TEST METHODS

The access floor manufacturer shall demonstrate the existence of a fully documented quality assurance program specifically established to ensure product performance required in Part 3 of this specification.

In addition, the access floor contractor shall provide certification of the Performance Requirements set out herein, on randomly selected, standard product using Test Methods summarised below.

MOB PF2 Standard Tests

The tests for Extra Heavy Grade Access Floor Systems shall be carried out and certified under Test Methods

MOB PF2 PS/SPU Platform (Raised Access) Floors Performance Specification.

5. SITE & INSTALLATION

Qualification

The access floor system and accessories to be installed by the manufacturer's authorised representative to maintain the integrity of the products and acceptable performance of the completed installation.

Inspection

Examine the sub-floor for unevenness, irregularities and dampness that could effect the quality and execution of the work.

Do not proceed with installation until the sub-floor surface is clean, dry, clear of the other trades and ready to receive access flooring.

Preparation & Installation

The access floor is to be prepared and installed in accordance with the access floor manufacturer's instructions, covering preparation, layout, alignment, and installation.

Level & Fit

The installed access floor shall be level within 1.5mm in 3 metres or 3.0mm over the entire floor and shall be rigid and free of rocking panels.

The perimeter fit of cut panels around perimeters, columns and other such structures shall have a maximum gap of 2mm but the system shall not rely for it's lateral stability on such structures.

Edge Treatment

Cut edges of panels shall be sealed in accordance with the access floor manufacturer's instructions.

Adjust and Clean

The access floor contractor shall remove access floor installation debris as work progresses, maintaining the area under finished panels in a clean condition.

The general contractor/builder will provide protection to the finished access floor to prevent damage from misuse.

Maintenance and Hand-over

On completion the access floor contractor shall provide a 'Care and Maintenance Manual'  which shall provide clear instruction for maintenance personnel in the safe use, cleaning and application of the access floor.